## DHW usage
DHW					Specific heat of water :	4.185	(kJ/kgC)	Jg-1C-1
		tank temp(C)	60				or	0.00116	(Kwh/kgC)					3
		bath temp(C)	37			shower flow(l/m)		8		bath depth(cm)	15			2.0925
		shower temp(C)	42			shower time (m)		6		length(m)	1.35			10
		mains temp(C)	10					width(m)	0.54

		tot vol	HW vol
	bath	98	53
	shower	64	40.96					Energy stored in tank down to:	50	C
	dishwasher	20	0					(Kwh)
	washMC		56					Tank temp
	handwash	1	0.5				tank size	60	40	60	80
				100	1.2	−1.2	1.2	3.5
Avg. Annual use			#people:	2			130	1.5	−1.5	1.5	4.5
	per person		household				160	1.9	−1.9	1.9	5.6
	#/day	#/wk	#/wk				190	2.2	−2.2	2.2	6.6
				usage(l)			220	2.6	−2.6	2.6	7.7
Bath		1		5527			250	2.9	−2.9	2.9	8.7
shower	0.8571429		0	25629			280	3.3	−3.3	3.3	9.8
dishwash			2	0			310	3.6	−3.6	3.6	10.8
washMC			1	2912			340	4.0	−4.0	4.0	11.9
hands	2			730			370	4.3	−4.3	4.3	12.9
other(l)			10	520			400	4.6	−4.6	4.6	13.9
	l/d/person:	50		35318			450	5.2	−5.2	5.2	15.7
			Kwh/yr	2052.8729			500	5.8	−5.8	5.8	17.4
			Kwh/day	5.6			600	7.0	−7.0	7.0	20.9
	Gas	6	p	£123			700	8.1	−8.1	8.1	24.4
	Electric	11	p	£226			800	9.3	−9.3	9.3	27.9
				900	10.5	−10.5	10.5	31.4
				1000	11.6	−11.6	11.6	34.9
				1500	17.4	−17.4	17.4	52.3
				2000	23.2	−23.2	23.2	69.7
				2500	29.1	−29.1	29.1	87.2
				3000	34.9	−34.9	34.9	104.6

## Monthly overview
Monthly Spread
Roof/Panel angle	30					Heating hours:	6
Panel size(tubes)	40		area:	2.9				Extra heating hours (work@home):	6

Stove output(KW)	4
HW output temp	50

(per month if not stated)	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	tots/avgs	gas cost	elec cost
Days away	0	14	2		14	4	14		2		2		52
Daytime working days	12	6	11	12	6	10	6	12	11	12	11	12	121
Heating hours/day	8.5	4.5	7.9	8.5	4.5	0.0	0.0	0.0	7.9	8.5	7.9	8.5	5.5
Heating hours	254.5	134.5	236.5	254.5	134.5	0	0	0	236.5	254.5	236.5	254.5	1996.5

Solar:
Insolation (Kwh/m2/day)	0.6	1.17	1.94	3.22	4.17	5	4.44	3.61	2.78	1.67	0.78	0.47	29.89
(from panelangle sheet (Kwh/m2/day)	0.9	2.9	2.9	2.9	4.54	4.54	4.54	2.9	2.9	2.9	0.9	0.9	33.72
Heat to panel (Kwh/day)	1.9	3.4	5.6	9.3	12.1	14.5	12.9	10.5	8.1	4.8	2.3	1.4
Heat to panel (Kwh)	79	103	171	284	368	441	392	318	245	147	69	41	2659	160	293

DHW usage (l)	2943	1589	2750	2943	1589	2556	1589	2943	2750	2943	2750	2943	30287
Mains water incoming temp (C)	4	5	7	9	12	14	15	14	12	9	7	5	9.4
Water Heating requirement (Kwh)	157	83	137	140	70	107	65	123	121	140	137	154	1436	86	158

Avg outside temp (Cam, 2006. C)	4	3.8	4.7	9.1	13.1	17.9	21.6	17.1	18	13.7	8	6.3	11.4
Space Heating avg power(whole house) (Kw)	3.9	4.0	3.7	2.8	2.0	1.0	0.3	1.1	0.9	1.8	3.0	3.3	2.3
Space Heating requirement (kwh)	993	538	875	713	269	0	0	0	213	458	710	840	5608	336	617
Space Heating avg power (lounge)(Kw)	2.3	2.3	2.3	1.9	1.2	0.3	0.0	0.4	0.3	1.1	2.0	2.1
Space Heating requirement (kwh)	585	309	544	484	161	0	0	0	71	280	473	534	3442	207	379

Stove hours (per day)	6.0	4.5	6.0	6.0	4.5	0.0	0.0	0.0	6.0	6.0	6.0	6.0
Solar provided (Kwh)	64	83	137	227	294	353	313	255	196	118	55	33	2128	128	234
Solar useable (Kwh)	64	83	137	227	294	107	65	123	196	118	55	33	1501	90	165
Solar fraction for DHW	0.40	0.99	1.00	1.62	4.19	3.30	4.85	2.07	1.62	0.84	0.40	0.22
Solar space heating (Kwh)	0	0	0	87	224	246	249	132	75	0	0	0	1012	61	111
Solar space heating useable (Kwh)	0	0	0	87	161	0	0	0	71	0	0	0	319	19	35
Stove provided (Kwh)	730	294	682	730	294	0	0	0	682	730	682	730	5555	333	611
Stove fraction for heating	0.74	0.55	0.78	1.02	1.09				3.20	1.59	0.96	0.87
Boiler Provided (Kwh)	356	244	194	0	0	0	0	0	0	0	110	231	1135	68	125
Solar fraction for heating	0.00	0.00	0.00	0.12	0.83				0.35	0.00	0.00	0.00	0.1
Heat to dump (Kwh)	0	0	0	0	0	0	117	57	75	0	0	0

## CH heatloss
				u-values (W/m2.K)
				now	pre-insul	window factor		0.17
Whole house approximation					wall(cavityfill)	0.46	1.85	avg air changes		1	/hr
				wall+PUR	0.15	0.46
				window	2	2	specific heat of air		0.33	W/m3K
				ext door	1.4	4	MHRV factor		0.2	(fraction of heat lost)
				roof	0.16	0.5
Size					floor	1.2	1.2
	Internal	External	windows	across	up			int wall	1.9
length(m)	8.22	8.83	north down					int door	5
width(m)	6.64	7.26	south down					bay roof	0.12	4
height(m)	2.4	5	north up					1st floor	2
floors	2		south up					solidwall+fill	1.85
				single-glazed window	5
	Area(m2)	temp diff	Heat loss(W/m2)	(pre-insul)
Wall	143	25	1366	5465				50mm PUR on inside	0.23
Window	24	25	1213	1213				75mm PUR inside	0.19
Floor	55	9	589	589				3G window	1
Roof	55	25	218	682				sunroom wall	0.13
total(W/K)			3387	7949				garage walls	0.20
	vol (m3)					block+block doorwall	0.27
Ventialtion	262	25	4323	4323		range(Kwh)	5240	13099
				12272
			7709	W	7.7	kW			imperial/metric conversion:	0.14422	(btu.in/hf.F.ft2 -> W/mK)
				material	k(btu.in/ hr.F.ft2)	k (W/mK)	R(1/k) (imperial)	R(1/k) (mK/W)
				As built:	1.85				polystyrene (cut edge)	0.25	0.038	4.00	26.32
U-values				Cavity fill:	0.46				polystyrene(smooth surface)	0.2	0.029	5.00	34.67
house wall	k (W/mK)	width(m)	R(m2K/W)	plus therm bd:	0.15				brick (outer leaf)	9	0.840	0.11	1.19
thermal bd	0.022	0.100	4.55					brick (inner leaf)		0.62
inside surface			0.13	0.13					plasterboard	4.5	0.210	0.22	4.76
plaster	0.210	0.018	0.09	0.09					mortar (inner leaf)		0.880		1.14
brick	0.620	0.102	0.16	0.16					mortar (outer leaf)		0.94		1.06
rockwool	0.04	0.065	1.63	0.00					rockwool		0.04		25.00
brick	0.840	0.102	0.12	0.12	improvement				phenolic foam		0.022		45.45
outside			0.04	0.04	factor:				fibreboard		0.1		10.00
		0.287	0.15	1.85	12.39				dritherm32		0.032		31.25
				multipro		0.26		3.85
Bay roof					7kN concrete block		0.19		5.26
felt	1	0.002	0.00	0.00					celcon block		0.11		9.09
plank	0.115376	0.012	0.10	0.10					softwood		0.13		7.69
fibreboard	0.1	0.018		0.18
kingspan	0.022	0.05	2.27
glasswool	0.04	0.13	3.25
polystyrene	0.038	0.1	2.63		improvement			Air-gaps			m2K/W
plasterboard	0.210	0.0095	0.05	0.05	factor:				cavity		0.180
			0.12	3.02	25.07				external surface (wall)		0.04
				internal surface (wall)		0.13
				external surface (roof)		0.04
Garage Wall					internal surface (roof)		0.1
inside			0.13	0.13					external surface (floor)		0.04
multipro 9mm	0.26	0.009	0.03	0.00					internal surface (floor)		0.17
recticel PIR+timber	0.022	0.05	2.27	0.00
Recticel PIR	0.022	0.05	2.27	0.00
brick	0.840	0.2	0.24	0.24
outside			0.04
			0.20	2.72

Garage door	outer frame	0.05	break width	0.03
	doorframing	0.1
	width	2.1	area	4.20
	height	2			total	local
	Cond(W/mk)	thickness	Rest(m2K/W)	Area (m2)	Area fraction	area fraction	layer
outside			0.04
Timber facing	0.15	0.05	0.33	3.9	0.93	1.00	1a
PIR	0.022	0.1	4.55	2.76	0.66	0.71	2a
ply	0.18	0.025	0.14	3.9	0.93		3a				area	Rupper	Rlower
Door frame	0.15	0.1	0.67	1.14	0.27	0.29	2b		doorframepath res	1.31	0.29
outer frame	0.15	0.15	1.00	0.30	0.07	1.00	4,6		doorinspath res	5.19	0.71	2.78
frame break	0.15	0.05	0.33	0.12	0.03	0.41	5a		sharedpath	0.64
outerframe@break	0.15	0.05	0.33	0.17	0.04	0.59	5b		bridgedpath	1.68			2.33
inside			0.13				Rmax	Rmin	Ravg		totalres	2.55
			doornom	0.19	Udoor:	0.39	2.78	2.33	2.55		U=	0.39
Max U (BS6946)					Uframe:	0.60	1.82	1.50	1.66
				Utot	0.41	2.46	2.46	2.46

Block+Block wall
inside			0.13
paster	0.26	0.02	0.08
thermal block	0.11	0.1	0.91
Rockwool	0.04	0.065	1.63
thermal block	0.11	0.1	0.91
outside			0.04
			0.27
Extension Wall
inside			0.13
plaster	0.26	0.02	0.08
block (dense)	0.19	0.1	0.53
Dritherm 32	0.032	0.2	6.25
brick	0.260	0.1	0.38
outside			0.04
			0.13

Thermal Mass
From SAP:	19	(Thermal Mass Parameter) Solid floor. maonry+dense plaster on all walls
floor	Y(W/m2K)			Thermal mass= Sum(area, addmittance(Y))/total floor area
concrete,carpet	3.2

Heatloss room by room					Total:	5661	9040
				Inc outerrooms:	8403	11782
Target temps
room	temp	air changes	MHRV factor
lounge	20	1.5	0.2
kitchen	17	2	0.2				Height of cavity blocked with crap (m)	0.4
hall	14	2	0.2
bog	18	1	0.2
bedroom	16	1	0.2
wookoffice	20	1.5	0.2
tessoffice	20	1.5	0.2
bathroom	23	2	0.2
unusedroom	10
unusedouterroom	8
workshop	18	2	0.4
airing cupboard	25	0.5	0.2
pottingshed	12	1	0.4
sunroom	20	1.5	0.4

Ground temp	11
outside design temp	-5
Ventilation temp	-5

Lounge		Tempdiff			heatloss		total
element	Area	(wholehouse)	(roomonly)	U-value	(wholehouse)	(roomonly)
External wall	15.2	25	25	0.15	57	57
Sunroom wall	7.3	0	12	0.46	0	41
External wall foot	4.8	25	25	1.85	222	222	278	278
Bay window	6.6	25	25	2	328	328
Window	2.3	25	25	2	113	113
ext glass door	1.8	0	12	2	0	44
kitchen wall	7.5	3	10	1.9	43	142
hall wall	12.0	6	10	1.9	136	227
floor	32.9	9	9	0.3	89	89
Ceiling (office)	13.3	0	10	2	0	267
Ceiling (to bed)	18.3	4	10	2	146	366
Bay window ceil	1.6	25	25	0.12	5	5
	vol			coeff	1138	1899	whole	roomonly
ventilation	78.9	25	25	0.495	977	977	2115	2876
				195	195	1334	2094
wookoffice
External wall(S)	6.1	25	25	0.15	23	23
External wall(W)	7.6	25	25	0.15	28	28	51	51
Window(S)	1.1	25	25	2	56	56
Window(W)	1.1	25	25	2	56	56
Door	1.5	6	6	2	17	17
T-office wall	4.3	0	10	1.9	0	82
Bed wall	8.7	4	10	1.9	66	166
Ceiling	14.2	25	25	0.16	57	57
floor	14.2	0	10	2	0	284
	vol			coeff	303	769	whole	roomonly
ventilation	32.6	25	25	0.495	404	404	707	1172
				81	81	384	849
tessoffice
External wall(N)	5.1	25	25	0.46	58	58
External wall(W)	5.2	25	25	0.46	60	60	118	118
Window(W)	1.1	25	25	2	56	56
W-office wall	4.3	0	10	1.9	0	82
Hall wall	5.5	0	10	1.9	0	104
Ceiling	7.2	25	25	0.16	29	29
floor	7.2	0	10	2	0	143
	vol			coeff	202	532	whole	roomonly
ventilation	16.5	25	25	0.495	204	204	406	736
				41	41	243	573
Bedroom
External wall(S)	6.8	21	21	0.46	66	66
External wall(E)	8.7	21	21	0.15	27	27	94	94
Window	2.3	21	21	2	97	97
W-office wall	9.9	-4	6	1.9	-75	113
Bathroom wall	4.0	-7	6	1.9	-53	45
Hall wall	2.3	2	6	1.9	9	26
Airing cupboard	2.3	-9	6	1.9	-39	26
Ceiling	17.9	21	21	0.16	60	60
Floor	17.9	-4	6	2	-143	214
	vol			coeff	-51	675	whole	roomonly
ventilation	41.1	21	21	0.33	285	285	234	959
				57	57	6	731
Bathroom
External wall(N)	4.0	28	28	0.15	16	16
External wall(W)	6.3	28	28	0.46	81	81	98	98
Window	1.1	28	28	2	62	62
Bedroom wall	2.3	7	13	1.9	30	57
Hall wall	5.5	9	13	1.9	94	136
Ceiling	7.2	28	28	0.16	32	32
Floor	7.2	6	13	2	86	186
	vol			coeff	402	571	whole	roomonly
ventilation	16.5	28	28	0.66	305	305	707	875
				61	61	463	632
Kitchen
External wall(N)	7.0	22	22	0.46	71	71
External wall foot(N)	1.7	22	22	1.85	71	71
External wall(W)	5.4	-3	9	0.46	-8	23
External wall foot(W)	1.1	-3	9	1.85	-6	18	128	182
Window	1.7	22	22	2	75	75
Window (Single-g)	0.6	22	22	5	62	62	137	137
Door	2.3	9	9	4	82	82
Lounge wall	8.6	-3	7	1.9	-49	115
Hall wall	6.5	3	7	1.9	37	87
Ceiling	10.3	-6	7	2	-123	144
Floor	10.3	6	6	0.3	18	18
	vol			coeff	230	764	whole	roomonly
ventilation	24.6	22	22	0.66	358	358	588	1122
				72	72	302	836
Hall/Bog
External wall(N)	12.0	19	19	0.46	105	105
External wall foot(N)	1.8	19	19	1.85	64	64
External wall(E)	3.5	23	19	0.46	37	30
External wall foot(E)	1.1	23	19	1.85	46	38	252	238
Window	1.1	23	19	2	51	42
Window	1.1	19	19	2	42	42
Ext Door	2.0	19	19	1.6	60	60
Lounge wall	10.8	-6	4	1.9	-124	82
Kitchen wall	5.4	-3	4	1.9	-31	41
Ceiling(t-office)	7.0	-6	4	2	-85	56
Ceiling(Loft)	6.1	19	19	0.16	18	18
Floor	10.2	3	3	1.2	37	37
	vol			coeff	221	616	whole	roomonly
ventilation	54.5	19	19	0.66	683	683	904	1299
				137	137	358	753

Workshop
Outside Wall	8.0	23	23	0.20	37	37
End (outside) wall	1.8	23	23	0.20	8	8
Party Wall	15.6	23	23	0.20	72	72
Roof Windows	1.2	23	23	2	55	55
Garage Door	4.2	23	23	0.50	49	49
Door	2.1	6	10	1.9	24	40
Roof	14.5	23	23	0.16	53	53
Pottingshed wall	6.4	6	10	1.9	73	122
Floor	14.5	7	7	0.3	30	30
	vol			coeff	401	466	whole	roomonly
ventilation	39.7	23	23	0.66	603	603	1004	1069
				121	121	522	586

Sunroom
Outside Wall (glazed)	5.8	25	25	0.20	29	29
Outside wall (E)	9.2	25	25	0.20	46	46
Glazing	10.8	25	25	0.90	244	244	272	272
Floor	27.0	9	9	0.15	36	36
Front Door	2.3	25	25	1.3	75	75
Roof	32.1	25	25	0.16	128	128
Pottingshed wall	10.7	8	12	1.9	162	244
Pottingshed door	2.1	8	12	1.9	32	48
Workshop door	2.1	8	12	1.9	32	48
Lounge wall	9.7	0	10	0.46	0	45
Kitchen wall	7.6	3	10	0.46	10	35
Bedroom wall	4.8	4	10	0.46	9	22
Bathroom wall	1.2	-3	10	0.46	-2	6
	vol			coeff	802	1005	whole	roomonly
ventilation	73.1	23	23	0.495	832	832	1635	1838
				166	166	969	1172

Pottingshed
Window	1.1	17	17	5.00	94	94
Party Wall	12.3	17	17	0.20	42	42
Roof Window	0.6	17	17	2	20	20
Door	2.1	-8	2	1.9	-32	8
Roof	16.0	17	17	0.16	44	44
Workshop wall	6.4	-6	4	1.9	-73	49
Sunroom wall	10.7	-8	4	1.9	-162	81
Floor	7.4	1	1	0.3	2	2
	vol			coeff	-66	339	whole	roomonly
ventilation	22.3	23	23	0.33	169	169	103	508
				34	34	-32	373

## Tank Losses
Tank losses		heat loss coefficient for storage tank:				0.1429	Btu/hr*ft2*F

Manufacturer		Navitron	Navitron	Navitron	Navitron	Navitron	Navitron	Navitron	Navitron	Navitron	Navitron
Tank volume (l)		120	135	172	210	144	168	216	259	320	450
Tank height (mm)		1050	1200	1500	1800	1050	1200	1500	1800	1800	1800
Tank Diameter (mm)		400	400	400	400	450	450	450	450	500	550
Insulation thickness (mm)		75	75	75	75	75	75	75	75	75	75
Surface area (m2)		1.6	1.8	2.1	2.5	1.8	2.0	2.4	2.9	3.2	3.6
k-value (W/mK)		0.020	0.020	0.020	0.020	0.020	0.020	0.020	0.020	0.020	0.020
R-value (K.m2/W)		3.8	3.8	3.8	3.8	3.8	3.8	3.8	3.8	3.8	3.8
U-value (W/K.m2)		0.27	0.27	0.27	0.27	0.27	0.27	0.27	0.27	0.27	0.27
Heat loss (W) @ temp diff	90	37.69
	80	33.50	37.52	45.57	53.61	38.45	42.97	52.01	61.06	68.68	76.47
	70	29.32	32.83	39.87	46.91	33.64	37.60	45.51	53.43	60.10	66.91
	60	25.13	28.14	34.17	40.20	28.83	32.23	39.01	45.80	51.51	57.35
	50	20.94	23.45	28.48	33.50	24.03	26.86	32.51	38.16	42.93	47.80
	40	16.75	18.76	22.78	26.80	19.22	21.48	26.01	30.53	34.34	38.24
	30	12.56	14.07	17.09	20.10	14.42	16.11	19.51	22.90	25.76	28.68
	20	8.38	9.38	11.39	13.40	9.61	10.74	13.00	15.27	17.17	19.12
	10	4.19	4.69	5.70	6.70	4.81	5.37	6.50	7.63	8.59	9.56

Heatloss (kWh) @50Cdiff,hrs	12	0.25	0.28	0.34	0.40	0.29	0.32	0.39	0.46	0.52	0.57
	24	0.50	0.56	0.68	0.80	0.58	0.64	0.78	0.92	1.03	1.15
From newark sheet (50mm)	24	1.3	1.39	1.6	1.8	1.45	1.58	1.84	2.05	2.34

			Tank energy input:
			From	to	diff	vol	energy
		top	28	65	37	20	0.86025
		tank4	27	57	30	20	0.6975
		tank3	26	63	37	20	0.86025
		tank2	25	57	32	20	0.744
		bottom	23	44	21	20	0.48825
							3.65025

## Sheet5
Current Usage
Leccy	Leccy
				Meter 1	read/estimated			Meter 2	read/estimated					price for		price		Kwh/day	£/day
Billdate	From	to	period	start		end		start		end		Meter1	Meter2	Total	1st		(rest)	cost
			(days)	(Kwh)		(Kwh)		(Kwh)		(Kwh)		Kwh	Kwh	Kwh	(pence)	Kwh	pence	£

					1481	146
		21/5/07 00:00				2647	r			6920	r
17/8/07 00:00	2007-May-21	17/8/07 00:00	88	2647	r	2731	r	6920	r	7126	r	84.0	206	290.0	11.066	217	7.975	29.83	3.30	0.34
	2007-08-17	19/11/07 00:00	94	2731	r	2870	r	7126	r	7474	r	139.0	348	487.0	11.066	232	7.975	46.01	5.18	0.49
4/3/08 00:00	2007-Nov-19	17/1/08 00:00	59	2870	r	2931	e	7474	r	7631	e	61.0	157	218.0	11.066	146	7.975	21.90	3.69	0.37
	2008-Jan-17	28/1/08 00:00	11	2931	e	2943		7631	e	7660		12.0	29	41.0	17.878	15	9.35	5.11	3.73	0.46
					0.0	0	0.0	11.066	0	7.975	0.00	#DIV/0!	#DIV/0!
					0.0	0	0.0	11.066	0	7.975	0.00	#DIV/0!	#DIV/0!

	Gas
	Pay first rate on	12.5	kWh/day					magic
Measured		12/1/07 00:00					calories	factor	4181	(annual total 2007)			110.9
	2007-Jan-12	27/1/07 00:00	15	6033		6059	r					39.3	31.6	820.4	3.56	188	2.732	23.97	56.80	1.60
	2007-Jan-27	4/2/07 00:00	8	6059		6064	r					39.3	31.6	157.8	2.979	100	2.192	4.25	23.67	0.53
	2007-Feb-04	11/2/07 00:00	7	6064		6068	r					39.3	31.6	126.2	2.979	88	2.192	3.46	22.54	0.49
	2007-Feb-11	24/2/07 00:00	13	6068		6071	r					39.3	31.6	94.7	2.979	163	2.192	2.82	9.71	0.22
	2007-Feb-24	11/3/07 00:00	15	6071		6074.2	r					39.3	31.6	101.0	2.979	188	2.192	3.01	8.84	0.20
	2007-Mar-11	3/5/07 00:00	53	6074.2		6075.6	r					39.3	31.6	44.2	2.979	664	2.192	1.32	1.43	0.02
	2007-May-03	30/6/07 00:00	58	6075.6		6075.9	r					39.3	31.6	9.5	2.979	727	2.192	0.28	0.71	0.00
	2007-Jun-30	30/9/07 00:00	92	6075.9		6076.8	r					39.3	31.6	28.4	2.979	1152	2.192	0.85	0.65	0.01
	2007-Sep-30	5/10/07 00:00	5	6076.8		6080.7	r					39.3	31.6	123.1	2.979	63	2.192	3.19	30.92	0.64
	2007-Oct-05	12/10/07 00:00	7	6080.7		6085.5	r					39.3	31.6	151.5	2.979	88	2.192	4.01	26.14	0.57
	2007-Oct-12	19/10/07 00:00	7	6085.5		6090.5	r					39.3	31.6	157.8	2.979	88	2.192	4.15	27.05	0.59
	2007-Oct-19	24/10/07 00:00	5	6090.5		6095.3	r					39.3	31.6	151.5	2.979	63	2.192	3.82	36.60	0.76
	2007-Oct-24	31/10/07 00:00	7	6095.3		6102.6	r					39.3	31.6	230.3	2.979	88	2.192	5.74	37.41	0.82
	2007-Oct-31	7/11/07 00:00	7	6102.6		6110.9	r					39.3	31.6	261.9	2.979	88	2.192	6.43	41.92	0.92
	2007-Nov-07	14/11/07 00:00	7	6110.9		6119.7	r					39.3	31.6	277.7	2.979	88	2.192	6.78	44.18	0.97
	2007-Nov-14	23/11/07 00:00	9	6119.7		6129.8	r					39.3	31.6	318.7	2.979	113	2.192	7.88	38.92	0.88
	2007-Nov-23	10/12/07 00:00	17	6129.8		6146.9	r					39.3	31.6	539.6	2.979	213	2.192	13.50	33.60	0.79
	2007-Dec-10	18/12/07 00:00	8	6146.9		6154.5	r					39.3	31.6	239.8	2.979	100	2.192	6.04	33.92	0.76
	2007-Dec-18	7/1/08 00:00	20	6154.5		6159.1	r					39.3	31.6	145.1	2.979	251	2.192	4.32	8.84	0.22
	2008-Jan-07	14/1/08 00:00	7	6159.1		6165.5	r					39.3	31.6	201.9	2.979	88	2.192	5.12	33.36	0.73

Gas					1177
					price for		price for
Bills		12/1/07 00:00				6033	r					calories		4152	1st	Kwh	rest	119.1
	2007-Jan-12	15/1/07 00:00	3	6033	r	6035	e					39.2085	31.5	63.04	4.959	38	2.801	2.59	21.01	0.86
	2007-Jan-15	15/2/07 00:00	31	6035	e	6069	r					39.2085	31.5	1071.68	3.560	401	2.732	32.60	34.57	1.05
	2007-Feb-16	21/5/07 00:00	172	6069	r	6075	r					39.2522	31.6	189.33	2.979	2154	2.192	5.64	1.10	0.03
	2007-May-22	2007-Aug-07	181	6075	r	6076	r					39.2522	31.6	31.56	2.979	2267	2.192	0.94	0.17	0.01
	2007-Aug-07	19/11/07 00:00	104	6076	r	6124	r					39.2510	31.6	1514.60	2.979	1303	2.192	43.45	14.56	0.42
	2007-Nov-19	17/1/08 00:00	59	6124	r	6165	r					38.8847	31.3	1281.65	2.979	739	2.192	33.91	21.72	0.57
	2008-Jan-18	8/2/08 00:00	21	6165	r	6175	r					38.8847	31.3	312.60	5.490	263	2.302	15.58	14.89	0.74
	2008-Feb-09		-39487	6175	r

					4175	(annual total 2007)			110.8
					1029	(annual total 2008)			29.0
					-195276	(annual total 2009)			4.9

Measured		12/1/07 00:00
	2007-Jan-12	27/1/07 00:00	15	6033		6059.0	r					820.4	3.56	188	2.732	23.97	54.69	1.60
	2007-Jan-27	4/2/07 00:00	8	6059		6064.0	r					157.8	2.979	100	2.192	4.25	19.72	0.53	Instaled wood-burner
	2007-Feb-04	11/2/07 00:00	7	6064		6068.0	r					126.2	2.979	88	2.192	3.46	18.03	0.49
	2007-Feb-11	24/2/07 00:00	13	6068		6071.0	r					94.7	2.979	163	2.192	2.82	7.28	0.22
	2007-Feb-24	11/3/07 00:00	15	6071		6074.2	r					101.0	2.979	188	2.192	3.01	6.73	0.20	Pilot light turned off
	2007-Mar-11	3/5/07 00:00	53	6074.2		6075.6	r					44.2	2.979	664	2.192	1.32	0.83	0.02
	2007-May-03	30/6/07 00:00	58	6075.6		6075.9	r					9.5	2.979	727	2.192	0.28	0.16	0.00
	2007-Jun-30	30/9/07 00:00	92	6075.9		6076.8	r					28.4	2.979	1152	2.192	0.85	0.31	0.01
	2007-Sep-30	5/10/07 00:00	5	6076.8		6080.7	r					123.1	2.979	63	2.192	3.19	24.61	0.64	Gunde Arrived - heating turned on
	2007-Oct-05	12/10/07 00:00	7	6080.7		6085.5	r					151.5	2.979	88	2.192	4.01	21.64	0.57
	2007-Oct-12	19/10/07 00:00	7	6085.5		6090.5	r					157.8	2.979	88	2.192	4.15	22.54	0.59
	2007-Oct-19	24/10/07 00:00	5	6090.5		6095.3	r					151.5	2.979	63	2.192	3.82	30.29	0.76
	2007-Oct-24	31/10/07 00:00	7	6095.3		6102.6	r					230.3	2.979	88	2.192	5.74	32.91	0.82
	2007-Oct-31	7/11/07 00:00	7	6102.6		6110.9	r					261.9	2.979	88	2.192	6.43	37.41	0.92
	2007-Nov-07	14/11/07 00:00	7	6110.9		6119.7	r					277.7	2.979	88	2.192	6.78	39.67	0.97
	2007-Nov-14	23/11/07 00:00	9	6119.7		6129.8	r					318.7	2.979	113	2.192	7.88	35.41	0.88	Gunde Left
	2007-Nov-23	10/12/07 00:00	17	6129.8		6146.9	r					539.6	2.979	213	2.192	13.50	31.74	0.79
	2007-Dec-10	18/12/07 00:00	8	6146.9		6154.5	r					239.8	2.979	100	2.192	6.04	29.98	0.76
	2007-Dec-18	7/1/08 00:00	20	6154.5		6159.1	r					145.1	2.979	251	2.192	4.32	7.26	0.22	New boiler working 2007-12-21
	2008-Jan-07	14/1/08 00:00	7	6159.1		6165.3	r					195.6	2.979	88	2.192	4.98	27.95	0.71	No woodburner - 2days all-day heating
	2008-Jan-14	22/1/08 00:00	8	6165.3		6168.0	r					85.2	2.979	100	2.192	2.54	10.65	0.32
	2008-Jan-22	28/3/08 00:00	66	6168		6176.8	r					277.7	2.979	827	2.192	8.27	4.21	0.13
	2008-Mar-28	6/4/08 00:00	9	6176.8		6176.8	r					0.0	2.979	113	2.192	0.00	0.00	0.00
	2008-Apr-06	20/7/08 00:00	105	6176.8		6181.0	r					132.5	2.979	1315	2.192	3.95	1.26	0.04
	2008-Jul-20	24/9/08 00:00	66	6181		6181.0	r					0.0	2.979	827	2.192	0.00	0.00	0.00
	2008-Sep-24	4/12/08 00:00	71	6181		6183.2	r					69.4	2.979	889	2.192	2.07	0.98	0.03
	2008-Dec-04	10/12/08 00:00	6	6183.2		6184.4	r					37.9	2.979	75	2.192	1.13	6.31	0.19
	2008-Dec-10	10/12/08 00:00	0.25	6184.4		6185.2	r					23.7	2.979	3	2.192	0.54	94.66	2.17
	2008-Dec-10	28/12/08 00:00	18	6185.15		6186.0	r					26.8	2.979	225	2.192	0.80	1.49	0.04
	2008-Dec-28	9/1/09 00:00	12	6186		6188.6	r					82.0	2.979	150	2.192	2.44	6.84	0.20	On 12hrs for thermal survey
	2009-Jan-09	10/1/09 00:00	1	6188.6		6191.7	r					97.8	2.979	13	2.192	2.25	97.82	2.25
	2009-Jan-10	2/7/09 00:00	173	6191.7		6194.5	r					88.4	2.979	2167	2.192	2.63	0.51	0.02
	2009-Jul-02		-39996	6194.5					-195462.6	2.979	-500990	2.192	-8227.33	4.89	0.21

## UFH
Total pipe length	100
Pressure drop in pipes

Independent heating, old fashioned ventilation				Uncoverd
	Max power needed	Area		area
	W	m2	W/m2	m2	W/m2
Workshop	1069	13.2	80.9802546092839	8	134
Sunroom	1838	27	68.0684685078375
Lounge	2876	32.1	89.5800361224952
Kitchen	1122	10.2	110.023063539874	5	224
Bog	1299	7.07	183.781139023806
Wook office	1172	12.9	90.874948014818
Bathroom	875	4.3	203.547265878701

Independent heating, controlled ventilation
	Max power needed	Area		area
	W	m2	W/m2	m2	W/m2	Spacing	Pipe length
Workshop	586	13.2	44.4286546092839	8	73	0.150	101.000
Sunroom	1172	27	43.4058261078375
Lounge	2094	32.1	65.235436496327
Kitchen	302	10.2	29.5765612075649	5	60
Bog	753	7.07	106.483963198064
Wook office	849	12.9	65.8357145264459
Bathroom	632	4.3	146.875793060097

Type B floor (floating)		Use sectoin 6.3 eqns
Heating temp drop σ (°C)	10
Flow temp vV (˚C)	45
Return temp vR (°C)	35
Room temp vI (°C)	16
insulation full thickness Sh (m)	0.050
insulation min thickness Sl (m)	0.033
pipe spacing T (m)	0.150
pipe diameter D (m)	0.016
Pipe wall thickness (m)	0.002
eff. Insulation thickness, Sins (m)	0.048
Thickness of floor surface, Su (m)	0.012
Conductivity of floor surface, λE (W/mK)	0.260	(Multipro)
Pipe material conductivity, λR (W/mK)	0.350				PE-RT/Alu:	0.45
Ali plate thickness sWL (m)	0.0005				PE/Alu	0.35
Ali plate conductivity λWL (W/mK)	200				PB	0.22
Floor covering conductivity RλB (m2K/W)	0
Temp diff between water and room ∆θH	23.6					Exernal design temp			C	0	-5	-15
Insulating layer therm res Rl,ins (m2K/W)	1.339	(sins/lins)	Err:504			Required insulation resistance			m2K/W	1.25	1.5	2
Insulation conductivity lins(W/mK)	0.036
External design temp	0	Can be 0, -5 or -15

Design value qdes	73	heat load/surf area
heat Load Qn,f	586
Heating surface area Af (m2)	8

heat output Qf (W)	630	q * area	OK
specific thermal output q	79		B ⋅ Π( ai^i ) ⋅ ∆θH			q = B ⋅ aB ⋅ aT^mT ⋅ au ⋅ aWL ⋅ aK ⋅ ∆θH
Downward thermal output qu

System coeff B (W/m2K)	6.5		Section 6.6		for pipe therm res =0.35
Floor covering factor aB	0.610		1/(1+B*au*aT^mT*aWL*aK*Rλ,B*(1+.44*SQRT(T))
aT lookup from table A6	1.093		table A6					Su/λE	0.01	0.02	0.03	0.04	0.05	0.06	0.08	0.1	0.15	0.18
Pipe spacing corr factor mT	-1.00		(6)	1-(T/0.075)					aT	1.103	1.1	1.097	1.093	1.091	1.088	1.082	1.075	1.064	1.059
Covering factor au	0.992		(1/α + 0.045/1)/(1/α + Su/λE)
Heat exchange co-efficient α (W/m2K)	10.8
Heat conduction factor aWL	0.974		table A8
Table A8 row from kWL	9
bu	0.7		table A7			Table A7			T	0.05	0.075	0.1	0.15	0.2	0.225	0.3	0.375	0.45
						bu	1	1	1	0.7	0.5	0.43	0.25	0.1	0
Characteristic value KWL	0.82	0.80	KWL=(sWL*λWL+bu*Su*λE)/0.125
Contact Correction factor aK	0.95		table A9	Depends on pipe spacing		Yable A9			T	0.05	0.075	0.1	0.15	0.2	0.225	0.3	0.375	0.45
						aK	1	0.99	0.98	0.95	0.92	0.9	0.82	0.72	0.6

	-4.735				Table A8	for D=16mm	kWL		T	0.05	0.075	0.1	0.15	0.2	0.225	0.3	0.375	0.45
						0	1	aWL	0.86	0.644	0.533	0.415	0.357	0.34	0.3	0.278	0.265
						0.1	2	aWL	1	1.01	1.02	1.04	1.06	1.07	1.09	1.1	1.1
						0.2	3	aWL	0.937	0.865	0.821	0.745	0.688	0.663	0.592	0.558	0.555
						0.3	4	aWL	0.96	0.925	0.905	0.855	0.8	0.79	0.72	0.69	0.68
						0.4	5	aWL	0.98	0.964	0.94	0.895	0.86	0.84	0.78	0.78	0.78
						0.5	6	aWL	0.995	0.979	0.963	0.924	0.894	1.07	1.09	1.1	1.1
						0.6	7	aWL	0.998	0.984	0.972	0.945	0.921	0.908	0.87	0.86	0.86
						0.7	8	aWL	1	0.99	0.98	0.96	0.943	0.934	0.91	0.9	0.9
						0.8	9	aWL	1	0.995	0.988	0.974	0.961	0.955	0.94	0.93	0.93
						0.9	10	aWL	1	0.998	0.995	0.99	0.98	0.975	0.97	0.97	0.97
						1	11	aWL	1	1	1	1	1	1	1	1
						inf	12	aWL	1	1.01	1.02	1.04	1.06	1.07	1.09	1.1	1.1

## BOM
		Parts, prices, suppliers			coil		PHE for water+solar	PHE for DHW only
		DHW simple			2128.83		1936.86	2055.67
		Solar Circuit, 20 tubes			627.05		669.41325	627.05
		Tank+DHW			758		523.66725	684.83625
		Boiler			743.78		743.78	743.78

		DHW simple			2224.80		2256.46	2375.27
		Solar Circuit, 40 tubes			946.65		989.01325	946.65
		Tank+DHW			534.3665		523.66725	684.83625
		Boiler			743.78		743.78	743.78

		DHW+heating, vented					2559.55	2601.14
		Solar Circuit, 40 tubes					989.01325	946.65
		Tank+DHW					826.75625	910.71
		Boiler					743.78	743.78

		DHW+heating, vented, DPS	DPS: solar coil, inc anti-vacum, strainer					3200.31
		Solar Circuit, 40 tubes						946.65
		Tank+DHW						1509.875
		Boiler						743.78

		DHW+heating, combi					2794.84
		Solar Circuit, 40 tubes					989.01325
		Tank+DHW					885.2135
		Boiler					920.61

		DHW+heating, combi, DPS						3025.81
		Solar Circuit, 40 tubes						946.65
		Tank+DHW						1158.55
		Boiler						920.61

ref		item	spec	supplier	price		part number	Manufacturer	URL	Datasheet/info

Solar		20 tube 47mm panel		navitron	395
		fitting kit		navitron	9.5
	.	20 tube 47mm panel		eco-nomical	319.6		47-1500-20	chinese	http://eco-nomical.co.uk/SolarWaterProduct.htm
	.	fitting straps, stainless	9mm holes	eco-nomical	11.08
		10mm tube	35m coil	BES	41.83		6941		http://www.bes.co.uk/products/139.asp
		10mm tube	10m coil	navitron
	.	10mm tube	25m coil	screwfix	36
	.	HT armaflex 10mm	10m	navitron	30.5
	.	Expansion tank	18l	eco-nomical	36.72			Zilmet
	.	Exp tank fitting kit	bracket, 500mm stainless flex (3/4"BSP F, QR valve	eco-nomical	22.03
		Antifreeze 5l	5l	Navitron	22		+ £21 delivery
		Antifreeze 5l	5l	eco-nomical	17.63
		High temp air bleed valve	3/8" BSP M, F	eco-nomical	29.38
		pump 12V 1.3A Craig	Brushless,20mm OD spigot	ebay - easy_flow_pumps	64		inc £4 delivery and £5connectors	Daviescraig	http://myworld.ebay.co.uk/easy_flow_pumps/	http://www.daviescraig.com.au/main/display.asp?pid=27
		12V supply		ebay - imikhan786	13				http://search.ebay.co.uk/_W0QQsassZimikhan786
		Filler (modified sprayer)		eco-nomical	25.56
	.	Filler (modified sprayer)		navitron	25
	.	Fill/drain valves	15mm OD barbs 1/2" BSP F 3/4" BSP M	eco-nomical	29.28
		Pressurised kit			69		88.03
		20mmrubber/10mm brass fittings
	.	PHE	Vaillant	ebay	40
		PHE	Vaillant 06-4950	abotuk.co.uk	46.87075		HE113	Vaillant	http://abcotuk.co.uk/Product.asp?ProductId=P217&Catid=C2
		PHE	Vaillant	abotuk.co.uk	34.385		HE110
	.	PHE fittings	15mm elbow*2+Tee		7.97825
		3-way valve	3-way, 22mm	hav.co.uk	63.48		honeywell
		Zone valve	2-way 22mm	honeywell	45		honeywell
		3-way valve	3-way, 22mm	ebay	40
		Zone valve	2-way 22mm	ebay	30
		Zone valve	2-way 22mm	abcot uk	26.9075			ORKLI	http://www.abcotuk.co.uk/Product.asp?ProductId=P536&Catid=C2
		3-way valve		abcot uk
		solenoid valve		hav.co.uk	45
		Anti-scale device			50

Tank		tank 123l twin coil	1050*400, 75mm insul	navitron	428
		123l thermal store, twin coil	inc expansion vessel, mixervalve	navitron	758
		tank 210l, twin coil	1800x400,75mminsul	navitron	498
		210l thermal store, twin coil	inc expansion vessel, mixervalve	navitron	818
		210l store, no coils	1500x450, 75mm ins, 3 diffusers, 7 ports	newark	341.831		tim quote
		123l store, no coils	1050*400, 75mm ins, 3 diffusers, 7 ports	newark	266.831
		210l store, no coils	1500*450, 75mmins, 5sensor,10boss	newark	534.3665
		210l store, solar coil	1500*450, 75mmins, 5sensor,10boss	newark	618.32025
		210l store, boiler coil	1500*450, 75mmins, 5sensor,7boss	newark	589.69725

DHW		PHE	100kW	DPS	76.375
		Flow switch		DPS	35.25
		Pump	45W, DAB VA55/130	bes	30.08		13926
		TMV, 22mm	40l @1bar	hav	47.32		HEAT219058	RWC UFH	http://www.hav.co.uk/products/shw-detail.asp?pid=12917&cid=996	http://www.rwc.co.uk/Public/tmv/22mmUFH.pdf
		TMV, 22mm		Navitron	39
		Expansion tank	8l	BES	18.941		11350
		TMV, 22mm	20l @1bar	ebay	25			Triton

		Boilers - open vent
		Veissman Vitodens 100	18kW	inspired heating	714.4		7179919	veissman	http://www.inspiredheating.co.uk/acatalog/VIESSMANN_CONDENSING_BOILERS.html
		Flue		inspired heating	58.75		7184319	veissman	http://www.inspiredheating.co.uk/acatalog/VIESSMANN_CONDENSING_BOILERS.html
		Veissman Vitodens 100	18kW	bhl	690.9		7179920		http://www.bhl.co.uk/product/VMAN_VDENS100_24HE_OV_BLR_WB1A102_9919
		Flue		bhl	52.88		7184319	veissman	http://www.bhl.co.uk/product.php?productid=7229&page=1
		Bruderus 600	11KW	inspired heating	639.4			bruderus	http://www.inspiredheating.co.uk/acatalog/BUDERUS_600_REGULAR_RANGE_CONDENSING_BOILERS.html
		Flue		inspired heating	58.75		T000083702 / 7716191106	bruderus
		Atmos interopen HE22	22KW		635.9805			atmos	http://www.tbsmerchants.co.uk/cgi-bin/build/product/PGAT.html
		Flue
		Vaillant Ecotex 415	15Kw

		Veissmann Vitodens 200 Combi			875.61
		Veissmann Vitodens 100 Combi			807.23
		Flue			45
		Vaillant
		Atmos intercombi
Controls		Flowmeter	Digital, for solar loop	flowmeters.co.uk	39			email

		22mm compression elbow		b.e.s	1.60975		17687
		22mm compression tee		b.e.s	2.19725		17661
		pump isolating ball valves		b.e.s	2.78475		8132

		Y-pattern strainer		b.e.s	9.81125

Pipe
		Copper 22mm	3m	b.e.s.	12.2435		10312
			2m	b.e.s.	12.145		10311
		Copper 15mm	3m	b.e.s.	6.12175
			3m	ridgeons	5.0055
			2m	b.e.s.	4.07725
			2m	ridgeons	3.337
		Hep20 15mm	50m	plumbworld	40.94				http://www.plumbworld.co.uk/298-0000

Rads
		Towel Rail 1800x600	White, curved, 756Watts	plumbworld	72.97

## orders
Plumbing orders
		ridgeons		51.8	b.e.s		52.9933333333333
item	number	code	price (ex)	cost	code	price (ex vat)
1"BSP parallel female tee	1	B161	1.93	1.93	6546	2.38	2.38
1"BSP parallel male to 22mm compression joiner	1	PX42	1.47	1.47	17637	1.41	1.41
1"BSP fibre washer	5			0	2415	0.11	0.55
1"BSP male cap	1	B185	0.95	0.95	6595	0.98	0.98
1"BSP taper Hex nipple	1	B144	1.01	1.01	6584	2.59	2.59
1"BSP parallel running nipple	1			0	6578	1.92	1.92
Boss White tub, 400g	1			0	6878	1.15	1.15
Hawk White jointing paste, 400g	1		1.98	1.98			0
1"BSP Stop cap	1	B147	0.8	0.8	6609	0.69	0.69
22mm copper tube, 3m	4		2.86	11.44	10312	3.4733333333333	13.8933333333333
15mm copper tube, 1m	12		1.43	17.16	10310	1.7366666666667	20.84	2
22mm yorkshire straight connector	8	YP21	0.44	3.52			0
22mm yorkshire elbow	2	YPS12	0.78	1.56			0
22mm compression connector	2	PX40	1.24	2.48	17590	1.24	2.48
22mm compression elbow	3	PX44	1.48	4.44	17687	1.37	4.11
Gas meter Flex connector 1" BS746 female swivel to 1" BSP male taper	1		3.06	3.06			0

	quantity	code	ex	inc
UFH1	https://www.underfloorheating1.co.uk				572.77
6-way manifold	1		218.67	262.404	262.404
Pump	0	?	0	0	0
Control pack	1		92	110.4	110.4
pipe, 16x2mm, 100m	0		75	90	0
pipe, 16x2mm, 200m	1		140	168	168
pipe, 16x2mm, 300m	0		210	252	0
			0	0	0
actuators		?	0	0	0
adaptors 16x1.8mm	12		2.22	2.664	31.968
blanking blugs	0	?	0	0	0

UFHtradedirect	http://ufhtradedirect.co.uk				726.22
6-way manifold	1		169	202.8	202.8
Pump+control pack	1		159	190.8	190.8
pipe 16x2mm, 50m	0		40	48	0
pipe 16x2mm, 100m	0		75	90	0
pipe 16x2mm, 200m	1		145	174	174
pipe 16x2mm, 500m	0		345	414	0
spreaders 1000 x 390, 3 slots, 120mm spacing	18		5.95	7.14	128.52
spreaders 1000 x 395, 2 slots, 200mm spacing	0		4.5	5.4	0
actuators		?		0	0
monoblocco adaptors 16x2mm	12		2.09	2.508	30.096
blanking blugs	8		0.99	1.188	9.504

BES	http://bes.co.uk				0.00
6-way manifold	1		0	0	0
Pump+control pack	1		0	0	0
pipe 16x2mm, 50m	0		0	0	0
pipe 16x2mm, 100m	0		0	0	0
pipe 16x2mm, 200m	1		0	0	0
pipe 16x2mm, 500m	0		0	0	0
spreaders 1000 x 390, 3 slots, 120mm spacing	18		0	0	0
spreaders 1000 x 395, 2 slots, 200mm spacing	0		0	0	0
actuators			0	0	0
monoblocco adaptors 16x2mm	12		0	0	0
blanking blugs	8		0	0	0

UFH Supply	http://www.ufhsupply.com/cat
6-way manifold (Ivar, inc adaptors, air valves, flow gauge)	1		262.8	315.36	315.36
Pump+control pack	1		0	0	0
pipe 16x2mm, 50m	0		0	0	0
pipe 16x2mm, 100m	1		165	198	198
pipe 16x2mm, 200m			230	276	0
pipe 16x2mm, 500m	0		0	0	0
spreaders 1000 x 390, 3 slots, 120mm spacing	18		0	0	0
spreaders 1000 x 395, 2 slots, 200mm spacing	0		0	0	0
actuators			0	0	0
blanking blugs	8		0	0	0

Grundfos Alpha2L 15-50	1		98	117.6	117.6			Anchor pumps	http://www.anchorpumps.com/pump-shop/manufacturers/grundfos/grundfos-alpha/grundfos-alpha2l-15-50-a-rated-eup-ready-domestic-circulator-240v
6-port manifold	1			200	200			Ebay	http://cgi.ebay.co.uk/ws/eBayISAPI.dll?ViewItem&item=120862182704&fromMakeTrack=true&ssPageName=VIP:watchlink:top:en

Brandon (beyond the stove)					312.972
Ivar manifold	1		75.6	90.72	90.72
200m pipe	1		146.09	175.308	175.308
500mpipe	1		365.22	438.264	438.264
eurocone	12		0.72	0.864	10.368
?	2		7.2	8.64	17.28
?	2		2.44	2.928	5.856
?	2		5.6	6.72	13.44
				0	0
				0	0

## Pipe Sizing
Pipe Sizing calcs

Gas
Section	Length	Extra lengthdue to fittings	Effective length	Boiler power	Required Gas flow rate	Pipe size	max length allowed	pressure loss	Progresive pressure loss	Notes
	m	m	m		m3/h	mm	m	mbar	mbar
Boiler	10.8	2	12.8	18	1.68	15	7	1.83	1.83	Too small
Boiler	10.8	2	12.8	18	1.68	22	30	0.43	0.43	OK
Boiler	10.8	2	12.8	27	2.52	22	26	0.49	0.49	OK

				Length of pipe (m)
			pipesize(mm)	3	6	9	12	15	20	25	30
			10	0.86	0.57	0.5	0.37	0.3	0.22	0.18	0.15
			12	1.5	1	0.85	0.82	0.69	0.52	0.41	0.34
			15	2.9	1.9	1.5	1.3	1.1	0.95	0.92	0.88
			22	8.7	5.8	4.6	3.9	3.4	2.9	2.5	2.3
			28	18	12	9.4	8	7	5.9	5.2	4.7

Water
Section	Length	Extra length due to fittings	Effective length	Boiler power	Required flow @20C delta	Pipe size		pressure loss		Notes
	m		m	kW	l/m	mm
Boiler loop	13	0.5	13.5	18	12.9	15
				8	5.7	15

section		heat transmission	temp diff	specific heat	flow rate	flow rate	pipe size	pressure loss	effective length	pressure needed
		kW	C	kJ/kgC	l/s	l/m	mm	Pa/m	m	Pa
boiler loop		18	20	4.186	0.2150023889154	12.9	22	260	13	3380
		8	20	4.186	0.0955566172957	5.7	15	410	13	5330
Rads	Emiter size	+20% for pipes	temp diff	specific heat	flow rate	flow rate	pipe size	pressure loss	effective length	pressure needed
pipe section	W	W	C	kJ/kgC	l/s	l/m	mm	Pa/m	m	Pa
A
B
C
D
E
F

solar loop
		2	14	4.186	0.0333333333333	2	10	300	13	3900
		0.2	3	4.186	0.0166666666667	1	10	180	13	2340
Optimal flow rates for diffusers/mantle:				0.15	0.2	0.15-0.2l/min/m2 ofpanel (Combisystem report)			0.435	0.58	l/min

		Flow Rate vs Pipe Size

		Flow rate (l/s)
Pressure loss		12mm	15mm	22mm	28mm	35mm	42mm	=pipe size
90		0.021	0.04	0.118
92.5		0.022	0.041	0.12
95		0.022	0.042	0.122
97.5		0.022	0.042	0.124
100		0.023	0.043	0.125
120		0.025	0.047	0.139
140		0.028	0.052	0.152
160		0.03	0.056	0.164
180		0.032	0.06	0.175
200		0.034	0.064	0.186
220		0.036	0.067	0.196
240		0.038	0.071	0.206
260		0.039	0.074	0.215
280		0.041	0.077	0.224
300		0.043	0.08	0.233
320		0.044	0.083	0.242
340		0.046	0.086	0.25
360		0.048	0.089	0.258
380		0.049	0.092	0.266
400		0.05	0.094	0.274
420		0.052	0.097	0.282
440		0.053	0.099	0.289
460		0.055	0.102	0.297
480		0.056	0.104	0.304
500		0.057	0.107	0.311
520		0.059	0.109	0.318
540		0.06	0.112	0.324
560		0.061	0.114	0.331
580		0.061	0.116	0.338
600		0.064	0.119	0.344

## Flow rates
Pipe sizes/volumes
	dia	int dia	area	length	vol					Expansion vessel sizing
	(mm)	(mm2)	(mm)	(m)	(l)					Number of Tubes	47mm	58mm
copper	28	26.2	539.129	1	0.54					40	0
copper	22	20.2	320.474	1	0.32					Manifold volume (l)	2.4
copper	15	13.6	145.267	1	0.15					Pipe lengths	10mm	12mm	15mm	22mm
copper	12	11.3	100.287	1	0.10					12	0	1	0.2
copper	10	8.8	60.8212	1	0.06					Pipe volume (l)	0.9
copper	8	6.8	36.3168	1	0.04					Heat exchanger type	phe	(enter 'coil' or 'PHE')
Hep2O	22	18	254.469	1	0.25		guessed wall thickness				PHE dimensions(mm)		190	50	90
Hep20	15	11.8	109.359	1	0.11					PHE volume (l)		0.4
Hep20	10	7.2	40.7150	1	0.04					Coil volume (l)		1.8
					Heat Exchanger Volume(l)	0.4
		flowrate	Velocity					Total System volume (l)	3.8
		l/m	m/s
copper	22	19	0.99					Specific steam power at stagnation (W/m2)		30
	15	15	1.72					Pipe dissipation at stangation (W/m)		25
	12	6	1.00					Total stagnation input power (W)	84.6
	10	3.6	0.99					Pipe length containing steam (m)	1.7	(each side)
	8	2.2	1.01
Plastic	22	5	0.33					Steam vol (l)	2.6
	15	5	0.76					Liquid in exp vessel (l)	0
	10	5	2.05					PRV setting (bar)	3
					Height from EV to PRV (m)	1
					EV preset (bar)	1.3

					EV capacitance	0.19

					Expansion vessel min volume (l)	15.4

## panels
Panel efficiency/cost
			special	price	width	length	height	aperture	absorber	gross area	loss coef a2	loss coef a1	Conversion factor	area	power	manifold vol
			£	£	mm	mm	mm	m2	m2	m2	W/(m2K2)	W/(m2K2)		m2	kWh/m2	l
Navitron SFB20				395	1466	1639		1.747		2.25	0.004	1.61	0.561	1.41	626	0.9	761
economical 47-1500-20			256.15	319.6	1610	1700	140	1.26	1.15	2.74					1	650	0.85413929040736
economical 58-1800-20					1.90	1.61		0.0083	2.085	0.573
			0.65	0.81				1.28

				η(x) = η0 – a1 * x – a2 * x^2 * Gk where x = (Tm – Ta) / Gk
				Gk = irradiation (W)
				Ta(Ambient Temp)
				Tm(Collector temp)

## PHE Energy
Sums on PHE energy transfer
	sensorA	sensorB	sensorC
	solin	solout	solout2		soldiff	mismatch	soldiff2		sensorC placed next to solout
	42.1	40.3	37.06		1.8	3.2	5.04
	41.1	40.1	33.06		1.0	7.0	8.04
	40.5	39.5	36.5		1.0	3.0	4
	40.4	39.3	35.3		1.1	4.0	5.1
	39.7	38.6	34.2		1.1	4.4	5.5
	39.1	37.9	34		1.2	3.9	5.1
					3.8
	solin	solout	solin2					sensorC placed next to solin
	38.38	37.44	38.38		0.9	0.0	0.94
	38.3	37.3	37.69		1.0	0.6	0.39
	38.25	37	37.5		1.2	0.8	0.5
	38.3	36.44	37.375		1.9	0.9	0.935
	38.3	35.8	37.3		2.5	1.0	1.5
	38.06	35.25	37.19		2.8	0.9	1.94
	24.56	31.43	22.8			0.8

	conclusion: sensor C reads 3.8C lower than sensorB and 0.8C lower than sensorA